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	(Product Code)：CB15500280
Model 

KFRI35GN-KORI35GN
Function 

COOLING

HEATING

Rated Voltage 

220-240V～
Frequency(Hz) (High/Standard /Low*)

95/68/25
95/74/25
Total Capacity (W) (High/Standard/Low *):

Total Capacity (Btu/h) (High/ Standard /Low*):

3800/3500/1220

12970/12000/4172

4740/4000/1310

14660/13650/4480

Power Input (W) (High/ Standard/Low*)

1560/1060/295

1420/1100/330

Rated Input (W) (High/ Standard *)

1600

1650

Rated Current (A) (High/ Standard *)

7.0

7.2

Air Flow Volume (m3/h) 

560
Dehumidifying Volume (l/h)

1.6
EER / C.O.P (W/W) 

2.44/3.3/4.14

3/3.64/3.97

Energy Class

A/A
Indoor  unit

Model of Indoor Unit

KFRI35GN
Fan Motor Speed (r/min) (H/M/L)

(1260)/1070/900/730

Output of Fan Motor (w)

20

Input Power of  Heater  (w)

/

Fan Motor Capacitor (uF)

1.0

Fan Motor RLA(A)

0.254

Fan Type-Piece

Cross flow fan – 1

Diameter-Length (mm)

φ92 X 645

Evaporator

Aluminum fin-copper tube

Pipe Diameter (mm)

7

Row-Fin Gap(mm) 

2-1.4

Coil length (l) x height (H) x coil width (L)

645X25.4X267

Swing Motor Model

MP24AA

Output of Swing Motor (W)

2.4

Fuse (A)

PCB 3.15A   

Sound Pressure Level dB (A) (H/M/L)

(41)/37/33/24

Sound Power Level dB (A) (H/M/L)***

(51)/47/43/34 ①
Dimension (W/H/D) ( mm)

845×275×180

Dimension of Package (L/W/H)( mm)

915×255×355
Net Weight /Gross Weight (kg)

11/14
Note：

1．Test  Standard：

2．*Inverter different Compressor speed

3．** Fan different speed
4．*** Approximate Calculation from Sound Pressure Level to Sound Power Level:

Average Sound Pressure Level
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：Sound pressure level of front test point
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：Sound pressure level of side test point，for indoor unit 
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Approximate Sound Power Lever
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	Outdoor unit
Model of Outdoor Unit

KORI35GN
Compressor Manufacturer/trademark 

MITSUBISHI

Compressor Model

KNB092FHBMC

Compressor Type

single-rotor

L.R.A. (A)

25
Compressor RLA(A)

8.9

Compressor Power Input(W)

895

Overload Protector

222KT-XH-2P-400mm

Throttling Method

Capillary throttling

Starting Method

Transducer starting

Working Temp Range (℃)

-10℃≤T≤43℃
Condenser 

Aluminum fin-copper tube 

Pipe Diameter (mm)

7

Rows-Fin Gap(mm)

2-1.4

Coil length (l) x height (H) x coil width (L)

608/498/22

Fan Motor Speed (rpm) (H/M/L)

880±20

Output of Fan Motor (W)

30

Fan Motor RLA(A)

0.3

Fan Motor Capacitor (uF)

2

Air Flow Volume of Outdoor Unit

/

Fan Type-Piece

Axial fan-1

Fan Diameter (mm)

400

Defrosting Method

Auto defrost

Climate Type

T1

Isolation

I

Moisture Protection

IP24

Permissible Excessive Operating Pressure for the Discharge Side(MPa)

3.8

Permissible Excessive Operating Pressure for the Suction Side(MPa)

1.2

Sound Pressure Level dB (A) (H/M/L)

≤54
Sound Power Level dB (A) (H/M/L)

≤64
Dimension (W/H/D) ( mm)

848X260X540

Dimension of Package (L/W/H)( mm)

878X360X580
Net Weight /Gross Weight (kg)

36/41

Refrigerant and Charge (kg)

R410A / 1.15
Connection Pipe

Length (m)

4

Gas additional charge(g/m)

15

Outer Diameter 

Liquid Pipe (mm)

Φ6(1/4”)

Gas Pipe (mm)

Φ12(1/2”)

Max Distance

Height (m)

5

Length (m)

10

Loading Quantity

20’ Container

Interior Dimensions L*W*H：5898*2352*2393，Door Opening W*H：2343*2280

90

40’ Container

Interior Dimensions L*W*H：12032*2350*2390，Door Opening W*H：2343*2280

192

40’ High Cube Container

Interior Dimensions L*W*H：12032*2350*2697，Door Opening W*H：2338*2585

216
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